## Description
This model assumes PV solar installations in the region of Ottawa, Canada
PV solar capabilities vary greatly by the amount of sunshine available during different months of the year. This spreadsheet illustrates the differences in each month.
The ultimate aim of the spreadsheet is to get a rough order of magnitude estimate of the amount of land area required for PV solar generation in Ontario. This assumes that ALL electricity is generated with PV solar (i.e. it ignores all other existing power sources)
Operation:
In the "Information" tab, select the month.
Based on the month, various values are looked up from the "Data Tables" tab. The source of each set of values is noted on this tab.
Based on the values, the following calculations occur:
* The energy demand curve for the shortest day of that month
* The PV solar generation curve for the shortest day of that month
* Hourly quantities of energy to be met with PV solar or stored energy.
* Area of PV solar panels
* Cost of solar installations and batteries
A few points:
* Solar looks reasonable in June, when The longest day of The year allows ample power to be generated during peak demand periods
* Solar looks rediculous in December, when the shortest day of the year creates massive bottlenecks for generation and storage
* The cost of energy storage is trillions of dollars, best case. At that cost, solutions that do not require storage are far more economical.
* It is possible to prorate these estimates by reducing the demands met by solar, assuming for example nuclear and/or hydro resources.
Copyright BWJK Consulting Corporation. All rights reserved.

## Information
Month | May
Monthly kWh/kW | 119 |  |  |  |  | User Input
Min Power (GW) | 10.5 |  |  |  |  | Lookups
Max Power (GW) | 20 |  |  |  |  | Calculations
Hours of daylight | 14.4
Sunrise (Digital and rounded) | 5.8 | 5
Sunset (Digital and rounded) | 20.1 | 21
Midday | 13
Daily Peak Generation Factor | 0.9058
PV Solar Generating Capacity | 58.3
ha per MW | 5.79 | From https://climateconnections.ca/app/uploads/2016/05/Kopan-Melisa.pdf
Total land area (km2) | 3375.57
Cost of PV Solar (Billions) | 58.3
Cost of Battery Storage ($US Billions) | 19891.2 | From https://www.nrel.gov/docs/fy19osti/73222.pdf, expected best case cost of battery storage in 2030
Demand met by
Hour of the Day | Load | Watts per Kilowatt of PV Solar | GW Generated | PV | Storage
0 | 12.4 | 0 | 0 | 0 | 12.4
1 | 11.925 | 0 | 0 | 0 | 11.925
2 | 11.45 | 0 | 0 | 0 | 11.45
3 | 10.975 | 0 | 0 | 0 | 10.975
4 | 10.5 | 0 | 0 | 0 | 10.5
5 | 10.5 | 0.101 | 5.8868 | 5.8868 | 4.6132
6 | 12.875 | 0.025 | 1.4571 | 1.4571 | 11.4179
7 | 15.25 | 0.151 | 8.8011 | 8.8011 | 6.4489
8 | 17.625 | 0.277 | 16.145 | 16.145 | 1.48
9 | 19.525 | 0.403 | 23.4889 | 19.525 | 0
10 | 19.525 | 0.528 | 30.7746 | 19.525 | 0
11 | 19.525 | 0.654 | 38.1185 | 19.525 | 0
12 | 19.05 | 0.78 | 45.4624 | 19.05 | 0
13 | 19.05 | 0.906 | 52.8063 | 19.05 | 0
14 | 19.05 | 0.78 | 45.4624 | 19.05 | 0
15 | 19.05 | 0.654 | 38.1185 | 19.05 | 0
16 | 19.525 | 0.528 | 30.7746 | 19.525 | 0
17 | 20 | 0.403 | 23.4889 | 20 | 0
18 | 20 | 0.277 | 16.145 | 16.145 | 3.855
19 | 20 | 0.151 | 8.8011 | 8.8011 | 11.1989
20 | 19.525 | 0.025 | 1.4571 | 1.4571 | 18.0679
21 | 17.625 | 0.101 | 5.8868 | 5.8868 | 11.7382
22 | 15.25 | 0 | 0 | 0 | 15.25
23 | 12.875 | 0 | 0 | 0 | 12.875
Total Energy (GWh) | 393.075 | 6.744 | 393.075 | 238.8799 | 154.1951

## Data Tables
Taken from https://www.energyhub.org/ontario/ On November 1, 2020
kWh/Kw
April | 115
August | 118
December | 52
February | 92
January | 66
July | 125
June | 124
March | 109
May | 119
November | 56
October | 86
September | 104
Min/Max Power for Ontario, taken from https://www.thinkingpower.ca/PDFs/Commentary/CCRE%20Commentary%20-%20Buying%20Electricity%20from%20Quebec%20-%20The%20Case%20Against%20New%20Intertie%20Capacity%20-%20April%202017.pdf
| Min | Max
April | 11 | 17.5
August | 11 | 22.5
December | 13.5 | 20.5
February | 15 | 21
January | 13.5 | 22
July | 11.5 | 23
June | 10.5 | 20
March | 12.5 | 20
May | 10.5 | 20
November | 12.5 | 20
October | 11 | 17.5
September | 10.5 | 21
Minimum Hours of Daylight, as computed from https://www.timeanddate.com/sun/canada/ottawa?month=3&year=2020, for Ottawa
| Hr | Min | Sec | Sunrise (hr) | Sunrise (min) | Sunset (hr) | Sunset (min) | Days in Month |  |  | Hrs | Sunrise (digital Hr) |  | Max Power per kW nameplate capacity, based on https://www.researchgate.net/figure/Typical-daily-output-curves-of-PV-in-different-seasons_fig3_318558683
April | 12 | 49 | 24 | 6 | 42 | 7 | 31 | 30 |  |  | 12.9 | 6.7 | 19.5 | 0.7971
August | 13 | 17 | 31 | 6 | 23 | 7 | 41 | 31 |  |  | 13.3 | 6.3 | 19.6 | 0.82609
December | 8 | 42 | 52 | 7 | 39 | 4 | 22 | 31 |  |  | 8.8 | 7.6 | 16.3 | 0.5
February | 10 | 3 | 59 | 7 | 24 | 5 | 9 | 28 |  |  | 10.1 | 7.4 | 17.1 | 0.5942
January | 8 | 47 | 25 | 7 | 42 | 4 | 30 | 31 |  |  | 8.8 | 7.7 | 16.5 | 0.5
July | 14 | 44 | 42 | 5 | 46 | 8 | 31 | 31 |  |  | 14.8 | 5.7 | 20.5 | 0.93478
June | 15 | 40 | 24 | 5 | 14 | 8 | 54 | 30 |  |  | 15.7 | 5.2 | 20.9 | 1
March | 11 | 10 | 28 | 6 | 40 | 5 | 50 | 31 | Note: Daylight savings time kicks in |  | 11.2 | 6.6 | 17.8 | 0.67391
May | 14 | 19 | 41 | 5 | 50 | 8 | 10 | 30 |  |  | 14.4 | 5.8 | 20.1 | 0.9058
November | 8 | 59 | 49 | 7 | 21 | 4 | 21 | 30 | Note: Daylight savings ends. Might be a worst case here as there's one more hour of nighttime power required… |  | 9 | 7.3 | 16.3 | 0.51449
October | 10 | 9 | 13 | 7 | 41 | 5 | 50 | 31 |  |  | 10.2 | 7.6 | 17.8 | 0.60145
September | 11 | 43 | 34 | 7 | 0 | 6 | 43 | 30 |  |  | 11.8 | 7 | 18.7 | 0.71739
[10 empty] | Min | 8.8
Hour | % of Additional Load, taken from https://energi.media/canada/ontario-electricity-demand-declining/ graph | [8 empty] | Max | 15.7
0 | 20
1 | 15
2 | 10
3 | 5
4 | 0
5 | 0
6 | 25
7 | 50
8 | 75
9 | 95
10 | 95
11 | 95
12 | 90
13 | 90
14 | 90
15 | 90
16 | 95
17 | 100
18 | 100
19 | 100
20 | 95
21 | 75
22 | 50
23 | 25